## cable calc
|  |  | Nominal supply voltage |  |  | Supply type- (AC or DC)
|  | Max allowable volts drop as percentage (%) | 13
[6 empty] | dc | [5 empty] | Voltage present at load
TOTAL |  |  | Vdrop allowable as a voltage |  |  | Min Cable Size |  |  | Min Cable Vdrop | Actual Vdrop | Cable Current Rating
LOAD - amps | Cable Length - m
10 | 10 | 5 | 0.65 | 0.0065 | 10 | 10mm2 |  | 0.0047 | 0.0047 V/M/A | 0.47 | 71A | 12.53
90C Cable rating (single phase)
[6 empty] | Vdrop/M/A | Size | Current rating
[6 empty] | 0.00058 | 95 | 290
Note: this is based on BS7211 LSOH 90C rated cable | [5 empty] | 0.00075 | 70 | 240
[6 empty] | 0.00105 | 50 | 189
[6 empty] | 0.00135 | 35 | 156
[6 empty] | 0.00185 | 25 | 126
[6 empty] | 0.0029 | 16 | 95
[6 empty] | 0.0047 | 10 | 71
[6 empty] | 0.0079 | 6 | 51
[6 empty] | 0.012 | 4 | 40
[6 empty] | 0.019 | 2.5 | 30
[6 empty] | 0.031 | 1.5 | 22
90C Cable rating (DC)
[6 empty] | Vdrop/M/A | Size | Current rating
[6 empty] | 0.00049 | 95 | 290
[6 empty] | 0.00068 | 70 | 240
[6 empty] | 0.00099 | 50 | 189
[6 empty] | 0.00135 | 35 | 156
[6 empty] | 0.00185 | 25 | 126
[6 empty] | 0.0029 | 16 | 95
[6 empty] | 0.0047 | 10 | 71
[6 empty] | 0.0079 | 6 | 51
[6 empty] | 0.012 | 4 | 40
[6 empty] | 0.019 | 2.5 | 30
[6 empty] | 0.031 | 1.5 | 22